# NESCOPHARM AFRICA  LIMITED

## STANDARD OPERATING PROCEDURE

### Title: Temperature and Humidity Mapping

SOP No: NSPL/SOP/WH/015
Version: 1.0
Effective Date: 01.10.2025
Review Date:    01.10.2026
Approved by: Managing Director

## 1. PURPOSE

To define the procedure for mapping temperature and relative humidity (RH) in storage areas to ensure that environmental conditions consistently comply with WHO Good Storage and Distribution Practices (TRS 1025) and protect product quality.

## 2. SCOPE

This SOP applies to all temperature- and humidity-controlled storage areas, including:

- Warehouses

- Cold rooms / refrigerators

- Freezers

- Transit areas affecting product storage

## 3. RESPONSIBILITY

| Position | Responsibility |
| --- | --- |
| Warehouse Manager | Ensures mapping is performed and maintained |
| Quality Manager | Reviews mapping data and verifies compliance |
| Responsible Person (RP) | Approves mapping plan and results |
| Maintenance / Technical Staff | Assist with placing sensors and recording data |
| External Contractors (if applicable) | Perform mapping using calibrated instruments |

## 4. DEFINITIONS

- Mapping: Systematic measurement of temperature and humidity at multiple locations within a storage area to identify variations.

- Data Logger: Device used for continuous recording of temperature and RH.

- Critical Control Point (CCP): Location where environmental conditions must be strictly monitored.

## 5. PROCEDURE

### 5.1 Planning

- Prepare a Temperature/RH Mapping Plan indicating:

  - Locations of sensors / data loggers

  - Frequency of measurements

  - Duration of study (e.g., 24–72 hours for mapping)

- Use calibrated equipment (see : NSPL/SOP/WH/014).

### 5.2 Execution

- Place data loggers at representative locations, including corners, middle, floor level, and near air vents.

- Record temperature and RH continuously during the mapping period.

- Ensure mapping is done under typical operational conditions (doors opening, HVAC operating).

### 5.3 Data Analysis

- Compare recorded values with required storage conditions.

- Identify hot or cold spots and areas of high humidity.

- Document deviations and assess risk to product quality.

### 5.4 Corrective Action

- Implement measures to correct identified environmental variations (e.g., adjust HVAC, reposition products).

- Document actions taken in CAPA system (NSPL/SOP/QA/007).

### 5.5 Approval and Review

- RP and Quality Manager review mapping results.

- Maintain mapping reports as part of compliance records.

- Repeat mapping periodically, whenever storage areas or equipment are changed, or after maintenance.

## 6. RECORDS / FORMS

| Record | Retention |
| --- | --- |
| Temperature/RH Mapping Plan | 5 years |
| Mapping Data / Graphs | 5 years |
| Corrective Action Records | 5 years |
| Review / Approval Records | 5 years |

## 7. REFERENCES

- WHO Technical Report Series 1025 – GSDP